	
[image: image1.png]§ PORT 4
(IR,




	Abandonment or Removal of Commercial Underground Tanks 

 Permit Application

CITY OF PORT ANGELES FIRE DEPARTMENT                                      
Attn: Fire Marshal           
102 E. Fifth St., Port Angeles, WA 98362                                                                            (360) 417-4653  Fax (360) 417-4659 
FireInspections@cityofpa.us




· Tanks utilized for SINGLE FAMILY RESIDENTIAL heating oil require Port Angeles Fire Department residential tank closure permit.
Contractor Performing Work ___________________________ Date ____________
Contractor Name _______________________________________________________
Contractor Address _____________________________________________________

Contractor Phone Number __________________ E-mail ________________________

Contractor UST ICC Certification Number_______________ Expiration Date ________

Contact Person _________________________________________________________
Tank Information
Site Name (if Applicable) _________________________________________________

Site Address ___________________________________________________________
Removal Date __________________________ Tank Construction Type ____________

Size of tank ____________________________ Type of fuel _____________________
Site Plan – drawn to scale that includes all of the following information: 

· Property Address or Parcel Number

· Property Owner’s name

· Property lines

· All building / structures

· Tank location(s)

· Piping

· Scale

· North arrow

Applicant Signature ____________________________________ Date ___________
Requirements and Limitations
Issuance of permit subject to compliance with recognized standards, listed requirements and approval by a field inspection from the Port Angeles Fire Department.
Date   Initial

____  ____
Provide one fire extinguisher with a minimum rating of 40-B-C. 

____  ____ 
There shall be no welding/ cutting or other sources of ignition in the area while abandoning operations are in progress.  Welding or cutting on tank require a Hot Work permit from the Port Angeles Fire Department.

____  ____
Washington State Department of Ecology Required 30 Day Notice.
____  ____
SEPA review – required if tank(s) exceeds 10,000 gallon capacity or the tank is located in a critical area. 

____  ____
A certification must be submitted by one of the following qualified persons, stating that the cleaned tank is inert and no longer hazardous: 

· Certified Marine Chemist

· Certified Industrial Hygienist

· Certified Safety Professional

· A technician working under their direct supervision of one of the aforementioned certified individual

The certification shall be accompanied by an inspection report verifying that all visible deposits, sludge or other foreign matter have been removed from the tank; that there is no discernable odor present; and that the final rinse from the tank cleaning did not include any visible sheen. 

____  ____
If tank is to be removed, shall adhere to IFC Section 5704.2.14.1. Removal of above-ground and underground tanks shall be in accordance with all of the following: 

1. Flammable and combustible liquids shall be removed from the   tank and connected piping.

2. Piping at tank openings that is not to be used further shall be disconnected.

3. Piping shall be removed from the ground.

Exception: Piping is allowed to be abandoned in place where the fire code official determines that removal is not practical. Abandoned piping shall be capped and safeguarded as required by the fire code official.

4. Tank openings shall be capped or plugged, leaving a 1/8-inch to 1/4-inch-diameter (3.2 mm to 6.4 mm) opening for pressure equalization.

5. Tanks shall be purged of vapor and inerted prior to removal.

6. All exterior above-grade fill and vent piping shall be permanently removed.

Exception: Piping associated with bulk plants, terminal facilities and refineries.

____  ____
If the tank must be stored on site, the tank shall be placed in a secure location and blocked to prevent movement.  The tank would also be required to be inerted a second time be transported.  

____  ____
Refill hole with suitable material ( earth, sand, etc.)

____  ____
If tank is to be abandoned in place, shall adhere to IFC Section 5704.2.13.1.4.  Tanks abandoned in place shall be as follows:

1. Flammable and combustible liquids shall be removed from the tank and connected piping. 

2. The suction, inlet, gauge, vapor return and vapor lines shall be disconnected.

3. The tank shall be filled completely with an approved inert solid material.

4. Remaining underground piping shall be capped or plugged 
5. A record of tank size, location and date of abandonment shall be retained.

6. All exterior above-grade fill piping shall be permanently removed when tanks are abandoned or removed.

Additional comments and/or requirements ____________________________________

__________________________________________________________________________________________________________________________________________________________________________________________________________________

	I have read and understand the requirements of this application.



	Applicant’s Signature: 

	Date:
	To be completed by city of Port Angeles: 
Permit #: 


For City Use Only


Date Received: _____________


Permit #: __________________








Page 3 of 3

_1252735181.bin

